FE11K (DIAD)

Front End
Control System
Commissioning Test Procedure

History:

Revision	Date	Who	Comments
1.00	02/03/18	Ian Gillingham

# Scope
This procedure is intended as a guide to commissioning Front End control systems. The scope is the verification and validation of software, electronics and associated subsystems directly affecting the Front End EPICS application.

# Safety Issues
Risk assessments and method statement (SB0140-RSK-CONT-053.doc) should be consulted prior to commissioning.

# Aspects
## Pre-checks

Network	The primary network connection should be patched from the fan-out unit (port 4) to the Ethernet port on the processor card	
Server	Before power-up, check kickstart installation has correct configuration.	
Stepper Drive Amplifier	Ensure the current limits are set appropriately via the drive amplifier module dip-switches	

## Vacuum
### Valves
Much of the valve commissioning procedures are detailed in EENG-PROT-TMP-0013
Test	Result

Connect dummy valves to the valve cables: Operate each valve individually via EPICS / Valve 01 Valve 02 Valve 03 Valve 04 / Valve 05 Valve 06 Fast Flap	Pass  Fail 

### Gauges
Test	Result
With the gauge controllers switched on, check the EPICS channels are connected to the correct gauge controller, by temporarily switching off each controller in sequence. The display mimic should eventually turn white (off-line) for the device. / Channel CC B1 A1 B2 / FE07B-VA-GCTLR-01 IMG-01 PIRG-01 IMG-02 PIRG-02 / FE07B-VA-GCTLR-02 IMG-03 PIRG-03 IMG-04 PIRG-04 / FE07B-VA-GCTLR-03 IMG-05 PIRG-05 IMG-06 PIRG-06 / FE07B-VA-GCTLR-04 IMG-07 PIRG-07 IMG-08 PIRG-08	Pass  Fail 

### Pumps

Test	Result
With the pump controllers switched on, check the EPICS channels are connected to the correct MPC, by temporarily switching off each MPC. The display mimic should eventually turn white (off-line) for the device. / Channel IONP / FE07B-VA-MPC-01 IONP-01 IONP-02 / FE07B-VA-MPC-02 IONP-03 IONP-04 / FE07B-VA-MPC-03 IONP-05 IONP-06 / FE07B-VA-MPC-04 IONP-07 IONP-08 / FE07B-VA-MPC-05 IONP-09	Pass  Fail 

## Absorbers
Test	Result
To be performed either with an assistant at the Front End and in contact via radio, or with the controlling PC at the Front End and connected to the primary EPICS network via Ethernet socket in the tunnel. / Actuate ABSB-01 – check movement and EPICS status / Actuate ABSB-02 – check movement and EPICS status / Actuate ABSB-03 – check movement and EPICS status	Pass  Fail  / Pass  Fail  / Pass  Fail 

## Temperature Sensors
Test	Result
Verify correct connection of PT100s by applying freezer spray, one at a time and checking the corresponding change on the application screen. / Apertures / Absorbers / PBPM temperature sensors are internal to the unit and unfeasible to individually vary the temperature. Temperatures are determined via a trip-amp and the value displayed on the application’s PBPM dialogue.	Pass  Fail  / Pass  Fail  / Pass  Fail 

## PBPM
No PBPMs fitted to this front-end.
## Cooling
### Water Flow Switches
Test	Result
Verify the operation and correct connection of water flow switches by examining the application’s ‘Cooling’ tab dialogue. Inhibiting water flow, then recommencing it in turn, should effect a change in status for each sensor on the display. / APTR-01 / APTR-02 / APTR-03 (where fitted) / APTR-04 (where fitted) / ABSB-01 / ABSB-02	Pass  Fail  / Pass  Fail  / Pass  Fail  / Pass  Fail  / Pass  Fail  / Pass  Fail  / Pass  Fail 

### Water Flow Switches
Test	Result
Verify the operation and correct connection of water flow switches by examining the application’s ‘Cooling’ tab dialogue. Inhibiting water flow, then recommencing it in turn, should effect a change in status for each sensor on the display. / Water Flow – 01 / Water Flow – 02 / Water Flow – 03 / Water Flow – 04 / Water Flow – 05	Pass  Fail  / Pass  Fail  / Pass  Fail  / Pass  Fail  / Pass  Fail 

### Rack Fans
Test	Result
Verify the operation and correct connection of rack fan alarms by examining the application’s ‘Cooling’ tab dialogue. Disconnecting the fan sensors in each the rack, should effect a change in status for each sensor on the display. / Rack Fan Alarm - 01 / Rack Fan Alarm - 02	Pass  Fail  / Pass  Fail 

## 3.7 Motion Control
Test	Axis Result
	X	Y
To be performed either with an assistant at the Front End and in contact via radio, or with the controlling PC at the Front End and connected to the primary EPICS network via Ethernet socket in the tunnel. / It is important to ensure, as far as possible, that the stepper drive wiring is correct. If not, there is potential that the motors could be damaged. / Check that only one (if any) of the limit switch LEDs are lit on the ‘Expert’ (EDM) panel. If both High and Low limits are on, then there is either a wiring fault, or the GeoBrick I/O polarity settings are incorrect. / Check for associated change in Raw Encoder Position. / As we are uncertain as to the exact position of the axis, set the limits to ±10mm, set ‘Use Encoder’ to ‘No’. / If already at a limit switch, drive away from it and check that the switch status changes. / Attempt to drive 1mm. / Verify with a vernier calliper that this is the distance travelled. / Home the axis using the Autohome edm utility. Raw encoder position should be reset to zero. / Set limits to the nominal limits for the Front End’s slits; / X: ±5mm the limits should be set to LLM 0.0 and HLM +10.0. / Y: ±5.0mm the limits should be set to LLM 0.0 and HLM +10.0. / Set to use encoder. / Use the Front End’s application, aperture dialogue to attempt to drive the axes through their extent of travel, checking that the relevant limit switches are actuated. / Repeat for all X and Y axes.	Pass  Fail  / Pass  Fail  / Pass  Fail  / Pass  / Fail  / Pass  Fail  / Pass  Fail  / Pass  Fail 