## GRIO-01
| FE10B-CS-VLVCC-01 - GRIO-01 | [7 empty] | Watchdog: |  | 1534.01
| Location: FE10B-CS-VLVCC01 Rack (CIA) | [7 empty] | GRT-PNT: |  | D1026
Module | Description | Module No. | I/O No. | Equipment | Sensor / Function | Interlock? | Logic | Full EPICS Designation | Raw | PLC Variable | Validated | PLC Variable | Set Point | PLC Variable | PLC Comment
GRT1-TS2P | Pt100 | 1 | 0 | FE10B-AL | APTR-01 |  |  |  | D 2100 | FE_RIO_01_RAW_TEMP_01 | D210 | FE_RIO_01_TEMP_01 | D110 | FE_RIO_01_ALARM_TEMP_01
|  |  | 1 | FE10B-AL | APTR-02 |  |  |  | D 2101 | FE_RIO_01_RAW_TEMP_02 | D211 | FE_RIO_01_TEMP_02 | D111 | FE_RIO_01_ALARM_TEMP_02
GRT1-TS2P | Pt100 | 2 | 0 | FE10B-AL | ABSR-01 |  |  |  | D 2102 | FE_RIO_01_RAW_TEMP_03 | D212 | FE_RIO_01_TEMP_03 | D112 | FE_RIO_01_ALARM_TEMP_03
|  |  | 1 | FE10B-AL | BPA-01 |  |  |  | D 2103 | FE_RIO_01_RAW_TEMP_04 | D213 | FE_RIO_01_TEMP_04 | D113 | FE_RIO_01_ALARM_TEMP_04
GRT1-TS2P | Pt100 | 3 | 0 | FE10B-AL | SLIT-01 |  |  |  | D 2104 | FE_RIO_01_RAW_TEMP_05 | D214 | FE_RIO_01_TEMP_05 | D114 | FE_RIO_01_ALARM_TEMP_05
|  |  | 1 | FE10B-AL | SLIT-02 |  |  |  | D 2105 | FE_RIO_01_RAW_TEMP_06 | D215 | FE_RIO_01_TEMP_06 | D115 | FE_RIO_01_ALARM_TEMP_06
GRT1-TS2P | Pt100 | 4 | 0 | FE10B-AL | ORIF-01 |  |  |  | D 2106 | FE_RIO_01_RAW_TEMP_07 | D216 | FE_RIO_01_TEMP_07 | D116 | FE_RIO_01_ALARM_TEMP_07
|  |  | 1 |  | SPARE |  |  |  | D 2107 | FE_RIO_01_RAW_TEMP_08 | D217 | FE_RIO_01_TEMP_08 | D117 | FE_RIO_01_ALARM_TEMP_08
GRT1-CT1 | Counter Inputs | 5 | 1 | [5 empty] | D 1010 | FE_RIO_01_RAW_COUNTER_IN_WORD1 | CIO 101 | FE_RIO_IN_COUNTER_IN_W1
[9 empty] | D 1011 | FE_RIO_01_RAW_COUNTER_IN_WORD2 | CIO 102 | FE_RIO_IN_COUNTER_IN_W2
|  |  |  | FE10B-HO | FLMTR-01 |  |  |  | D 1012 | FE_RIO_01_RAW_COUNTER_IN_WORD3 | CIO 103 | FE_RIO_IN_COUNTER_IN_W3
| Counter Outputs | [7 empty] | CIO 1000 | FE_RIO_01_RAW_COUNTER_OUT_WORD1 |  | FE_RIO_IN_COUNTER_OUT_W1
[9 empty] | CIO 1001 | FE_RIO_01_RAW_COUNTER_OUT_WORD2 |  | FE_RIO_IN_COUNTER_OUT_W2
[9 empty] | CIO 1002 | FE_RIO_01_RAW_COUNTER_OUT_WORD3 |  | FE_RIO_IN_COUNTER_OUT_W3
GRT1-ID4 | Digital IN | 6 | 0 | FE10B-CS | ABSR-01-FLOW SW |  |  |  | D 1013.00 | FE_RIO_01_RAW_DI_01 | CIO 104.00 | FE_RIO_01_DI_01
|  |  | 1 | FE10B-MP | ABSR-01-FLOW SW |  |  |  | D 1013.01 | FE_RIO_01_RAW_DI_02 | CIO 104.01 | FE_RIO_01_DI_02
|  |  | 2 | FE10B-CS | BPA-01-FLOW SW |  |  |  | D 1013.02 | FE_RIO_01_RAW_DI_03 | CIO 104.02 | FE_RIO_01_DI_03
|  |  | 3 | FE10B-MP | BPA-01-FLOW SW |  |  |  | D 1013.03 | FE_RIO_01_RAW_DI_04 | CIO 104.03 | FE_RIO_01_DI_04
GRT1-ID4 | Digital IN | 7 | 0 | FE10B-CS | SLIT-01-FLOW SW |  |  |  | D 1013.04 | FE_RIO_01_RAW_DI_05 | CIO 104.04 | FE_RIO_01_DI_05
|  |  | 1 | FE10B-MP | SLIT-01-FLOW SW |  |  |  | D 1013.05 | FE_RIO_01_RAW_DI_06 | CIO 104.05 | FE_RIO_01_DI_06
|  |  | 2 | FE10B-DI | FSCR-01-FLOW SW |  |  |  | D 1013.06 | FE_RIO_01_RAW_DI_07 | CIO 104.06 | FE_RIO_01_DI_07
|  |  | 3 | FE10B-MP | FSCR-01-FLOW SW |  |  |  | D 1013.07 | FE_RIO_01_RAW_DI_08 | CIO 104.07 | FE_RIO_01_DI_08
GRT1-ID4 | Digital IN | 8 | 0 | FE10B-CS | ORIF-01-FLOW SW |  |  |  | D 1013.08 | FE_RIO_01_RAW_DI_09 | CIO 104.08 | FE_RIO_01_DI_09
|  |  | 1 | FE10B-MP | ORIF-01-FLOW SW |  |  |  | D 1013.09 | FE_RIO_01_RAW_DI_10 | CIO 104.09 | FE_RIO_01_DI_10
|  |  | 2 | FE10B-CS | TPIP-01-FLOW SW |  |  |  | D 1013.10 | FE_RIO_01_RAW_DI_11 | CIO 104.10 | FE_RIO_01_DI_11
|  |  | 3 | FE10B-MP | TPIP-01-FLOW SW |  |  |  | D 1013.11 | FE_RIO_01_RAW_DI_12 | CIO 104.11 | FE_RIO_01_DI_12
GRT1-ID4 | Digital IN | 9 | 0 | SR10B-VA | FANC-01-FAN CONTROLLER |  |  |  | D 1013.12 | FE_RIO_01_RAW_DI_13 | CIO 104.12 | FE_RIO_01_DI_13
|  |  | 1 |  | PSU1-HEALTHY |  |  |  | D 1013.13 | FE_RIO_01_RAW_DI_14 | CIO 104.13 | FE_RIO_01_DI_14
|  |  | 2 | [5 empty] | D 1013.14 | FE_RIO_01_RAW_DI_15 | CIO 104.14 | FE_RIO_01_DI_15
|  |  | 3 | [5 empty] | D 1013.15 | FE_RIO_01_RAW_DI_16 | CIO 104.15 | FE_RIO_01_DI_16
GRT1-ROS2 | Relay Out | 10 | 0 | FE10B-VA | RGA-01-RESET |  |  |  | CIO 1003.00 | FE_RIO_01_RAW_DO_01 |  | FE_RIO_01_DO_01
|  |  | 1 | FE10B-VA | RGA-02-RESET |  |  |  | CIO 1003.01 | FE_RIO_01_RAW_DO_02 |  | FE_RIO_01_DO_02
GRT1-ROS2 | Relay Out | 11 | 0 | FE10B-VA | RGA-03-RESET |  |  |  | CIO 1003.02 | FE_RIO_01_RAW_DO_03 |  | FE_RIO_01_DO_03
|  |  | 1 | FE10B-VA | RGA-04-RESET |  |  |  | CIO 1003.03 | FE_RIO_01_RAW_DO_04 |  | FE_RIO_01_DO_04
GRT1-ROS2 | Relay Out | 12 | 0 | FE10B-VA | RGA-05-RESET |  |  |  | CIO 1003.04 | FE_RIO_01_RAW_DO_05 |  | FE_RIO_01_DO_05
|  |  | 1 | [5 empty] | CIO 1003.05 | FE_RIO_01_RAW_DO_06 |  | FE_RIO_01_DO_06
GRT1-AD2 | Analog IN | 13 | 0 | FE10B-VA | GCTLR-01-LOG/LIN AOUT A1 |  |  |  | D 2120 | FE_RIO_01_RAW_AI_01 | D 230 | FE_RIO_01_AI_01 | D 130
|  |  | 1 | SR10C-VA | GCTLR-02-LOG/LIN AOUT A1 |  |  |  | D 2121 | FE_RIO_01_RAW_AI_02 | D 231 | FE_RIO_01_AI_02 | D 131
GRT1-AD2 | Analog IN | 14 | 0 | FE10B-VA | GCTLR-03-LOG/LIN AOUT A1 |  |  |  | D 2122 | FE_RIO_01_RAW_AI_03 | D 232 | FE_RIO_01_AI_03 | D 132
|  |  | 1 | [5 empty] | D 2123 | FE_RIO_01_RAW_AI_04 | D 233 | FE_RIO_01_AI_04 | D 133
GRT1-ID4-1 | Digital IN | 15 | 0 | FE10B-VA | TCTLR-01-AT SPEED |  |  |  | D 1014.00 | FE_RIO_01_RAW_DI_17 | CIO 105.00 | FE_RIO_01_DI_17
|  |  | 1 | [5 empty] | D 1014.01 | FE_RIO_01_RAW_DI_18 | CIO 105.01 | FE_RIO_01_DI_18
|  |  | 2 | [5 empty] | D 1014.02 | FE_RIO_01_RAW_DI_19 | CIO 105.02 | FE_RIO_01_DI_19
|  |  | 3 | [5 empty] | D 1014.03 | FE_RIO_01_RAW_DI_20 | CIO 105.03 | FE_RIO_01_DI_20
GRT1-ROS2 | Relay Out | 16 | 0 | FE10B-VA | TCTLR-01-START |  |  |  | CI0 1003.06 | FE_RIO_01_RAW_DO_07 |  | FE_RIO_01_DO_07
|  |  | 1 | [5 empty] | CI0 1003.07 | FE_RIO_01_RAW_DO_08 |  | FE_RIO_01_DO_08

## GRIO-02
| FE10B-CS-VLVCC-01 - GRIO-02 | [7 empty] | Watchdog: |  | 1534.02
| Location: JN box 4 SR Cell 10 | [7 empty] | GRT-PNT: |  | D1026
Module | Description | Module No. | I/O No. | Equipment | Sensor / Function | Interlock? | Logic | Full EPICS Designation | Raw | PLC Variable | Validated | PLC Variable | Set Point | PLC Variable | PLC Comment
GRT1-TS2P | Pt100 | 1 | 0 | FE10B-AL | TMON-07 |  |  |  | D 2108 | FE_RIO_02_RAW_TEMP_01 | D 218 | FE_RIO_02_TEMP_01 | D 118 | FE_RIO_02_ALARM_TEMP_01
|  |  | 1 | FE10B-AL | EXST-01 |  |  |  | D 2109 | FE_RIO_02_RAW_TEMP_02 | D 219 | FE_RIO_02_TEMP_02 | D 119 | FE_RIO_02_ALARM_TEMP_02
GRT1-TS2P | Pt100 | 2 | 0 | FE10B-AL | EXST-02 |  |  |  | D 2110 | FE_RIO_02_RAW_TEMP_03 | D 220 | FE_RIO_02_TEMP_03 | D 120 | FE_RIO_02_ALARM_TEMP_03
|  |  | 1 | FE10B-AL | EXST-03 |  |  |  | D 2111 | FE_RIO_02_RAW_TEMP_04 | D 221 | FE_RIO_02_TEMP_04 | D 121 | FE_RIO_02_ALARM_TEMP_04
GRT1-TS2P | Pt100 | 3 | 0 | FE10B-AL | EXST-04 |  |  |  | D 2112 | FE_RIO_02_RAW_TEMP_05 | D 222 | FE_RIO_02_TEMP_05 | D 122 | FE_RIO_02_ALARM_TEMP_05
|  |  | 1 | FE10B-AL | EXST-05 |  |  |  | D 2113 | FE_RIO_02_RAW_TEMP_06 | D 223 | FE_RIO_02_TEMP_06 | D 123 | FE_RIO_02_ALARM_TEMP_06
GRT1-TS2P | Pt100 | 4 | 0 | FE10B-AL | EXST-06 |  |  |  | D 2114 | FE_RIO_02_RAW_TEMP_07 | D 224 | FE_RIO_02_TEMP_07 | D 124 | FE_RIO_02_ALARM_TEMP_07
|  |  | 1 | FE10B-AL | EXST-07 |  |  |  | D 2115 | FE_RIO_02_RAW_TEMP_08 | D 225 | FE_RIO_02_TEMP_08 | D 125 | FE_RIO_02_ALARM_TEMP_08
GRT1-TS2P | Pt100 | 5 | 0 | FE10B-AL | EXST-08 |  |  |  | D 2116 | FE_RIO_02_RAW_TEMP_09 | D 226 | FE_RIO_02_TEMP_09 | D 126 | FE_RIO_02_ALARM_TEMP_09
|  |  | 1 | FE10B-AL | EXST-09 |  |  |  | D 2117 | FE_RIO_02_RAW_TEMP_10 | D 227 | FE_RIO_02_TEMP_10 | D 127 | FE_RIO_02_ALARM_TEMP_10
GRT1-TS2P | Pt100 | 6 | 0 | FE10B-AL | EXST-10 |  |  |  | D 2118 | FE_RIO_02_RAW_TEMP_11 | D 228 | FE_RIO_02_TEMP_11 | D 128 | FE_RIO_02_ALARM_TEMP_11
|  |  | 1 | FE10B-AL | EXST-11 |  |  |  | D 2119 | FE_RIO_02_RAW_TEMP_12 | D 229 | FE_RIO_02_TEMP_12 | D 129 | FE_RIO_02_ALARM_TEMP_12
GRT1-ID4 | Digital IN | 7 | 0 | FE10B-RS | VALVE-11 READY |  |  |  | D 1015.00 | FE_RIO_02_RAW_DI_01 | CIO 106.00 | FE_RIO_02_DI_01
|  |  | 1 | FE10B-RS | VALVE-11 CLOSED WARNING |  |  |  | D 1015.01 | FE_RIO_02_RAW_DI_02 | CIO 106.01 | FE_RIO_02_DI_02
|  |  | 2 | SPARE |  |  |  |  | D 1015.02 | FE_RIO_02_RAW_DI_03 | CIO 106.02 | FE_RIO_02_DI_03
|  |  | 3 | SPARE |  |  |  |  | D 1015.03 | FE_RIO_02_RAW_DI_04 | CIO 106.03 | FE_RIO_02_DI_04
GRT1-ID4 | Digital IN | 8 | 0 | FE10B-SMC | VALVE-06 OPEN |  |  |  | D 1015.04 | FE_RIO_02_RAW_DI_05 | CIO 106.04 | FE_RIO_02_DI_05
|  |  | 1 | FE10B-SMC | VALVE-07 OPEN |  |  |  | D 1015.05 | FE_RIO_02_RAW_DI_06 | CIO 106.05 | FE_RIO_02_DI_06
|  |  | 2 | FE10B-SMC | VALVE-12 OPEN |  |  |  | D 1015.06 | FE_RIO_02_RAW_DI_07 | CIO 106.06 | FE_RIO_02_DI_07
|  |  | 3 | FE10B-SMC | VALVE-13 OPEN |  |  |  | D 1015.07 | FE_RIO_02_RAW_DI_08 | CIO 106.07 | FE_RIO_02_DI_08
GRT1-ID4 | Digital IN | 9 | 0 | FE10B-SMC | VALVE-14 OPEN |  |  |  | D 1015.08 | FE_RIO_02_RAW_DI_09 | CIO 106.08 | FE_RIO_02_DI_09
|  |  | 1 | FE10B-SMC | VALVE-15 OPEN |  |  |  | D 1015.09 | FE_RIO_02_RAW_DI_10 | CIO 106.09 | FE_RIO_02_DI_10
|  |  | 2 | FE10B-SMC | VALVE-16 OPEN |  |  |  | D 1015.10 | FE_RIO_02_RAW_DI_11 | CIO 106.10 | FE_RIO_02_DI_11
|  |  | 3 | FE10B-SMC | VALVE-17 OPEN |  |  |  | D 1015.11 | FE_RIO_02_RAW_DI_12 | CIO 106.11 | FE_RIO_02_DI_12
GRT1-ID4 | Digital IN | 10 | 0 | FE10B-SMC | VALVE-18 OPEN |  |  |  | D 1015.12 | FE_RIO_02_RAW_DI_13 | CIO 106.12 | FE_RIO_02_DI_13
|  |  | 1 | SPARE |  |  |  |  | D 1015.13 | FE_RIO_02_RAW_DI_14 | CIO 106.13 | FE_RIO_02_DI_14
|  |  | 2 | SPARE |  |  |  |  | D 1015.14 | FE_RIO_02_RAW_DI_15 | CIO 106.14 | FE_RIO_02_DI_15
|  |  | 3 | SPARE |  |  |  |  | D 1015.15 | FE_RIO_02_RAW_DI_16 | CIO 106.15 | FE_RIO_02_DI_16
GRT1-ROS2 | Relay Out | 11 | 0 | FE10B-RS | VALVE-11 CTRL MODE |  |  |  | CIO 1004.00 | FE_RIO_02_RAW_DO_01 |  | FE_RIO_02_DO_01
|  |  | 1 | FE10B-RS | VALVE-11 CLOSE DEMAND |  |  |  | CIO 1004.01 | FE_RIO_02_RAW_DO_02 |  | FE_RIO_02_DO_02
GRT1-ROS2 | Relay Out | 12 | 0 | FE10B-RS | VALVE-11 HOLD |  |  |  | CIO 1004.02 | FE_RIO_02_RAW_DO_03 |  | FE_RIO_02_DO_03
|  |  | 1 | FE10B-RS | VALVE11 OPEN DEMAND |  |  |  | CIO 1004.03 | FE_RIO_02_RAW_DO_04 |  | FE_RIO_02_DO_04
GRT1-ROS2 | Relay Out | 13 | 0 | SR10B-VA | ROOTS-01 RUN DEMAND |  |  |  | CIO 1004.04 | FE_RIO_02_RAW_DO_03 |  | FE_RIO_02_DO_03
|  |  | 1 | SPARE |  |  |  |  | CIO 1004.05 | FE_RIO_02_RAW_DO_04 |  | FE_RIO_02_DO_04
GRT1-AD2 | Analog IN | 14 | 0 | FE10B-RS | VALVE-11 POSITION |  |  |  | D 2124 | FE_RIO_02_RAW_AI_01 | D 234 | FE_RIO_02_AI_01 | D 134
|  |  | 1 | FE10B-RS | VALVE-11 PRESSURE |  |  |  | D 2125 | FE_RIO_02_RAW_AI_02 | D 235 | FE_RIO_02_AI_02 | D 135
GRT1-DA2V | Analog Out | 15 | 0 | FE10B-RS | VALVE-11 PRESSURE SET POINT |  |  |  | CIO 1005 | FE_RIO_02_RAW_AO_01 |  | FE_RIO_02_AO_01
|  |  | 1 | FE10B-RS | VALVE-11 SENSOR |  |  |  | CIO 1006 | FE_RIO_02_RAW_AO_02 |  | FE_RIO_02_AO_02

## EX-600 SMC
| FE10B-CS-VLVCC-01 - SMC-01 | [7 empty] | Watchdog: | 1534.02
Location: JN box 4 SR Cell 10
Module | Description | Module No. | I/O No. | Equipment | Sensor / Function | Interlock? | Logic | Full EPICS Designation | Raw | Validated | Set Point | PLC Variable | PLC Comment
EX600-SPN# | EX600 SOL VALVES (Output Area) | 1 | 1 | Valve-06 |  |  |  |  | CIO 1007.00 |  |  | V6_SOLENOID | V6 SOLENOID
|  |  | 2 | Valve-07 |  |  |  |  | CIO 1007.01 |  |  | V7_SOLENOID | V7 SOLENOID
|  |  | 3 | Valve-12 |  |  |  |  | CIO 1007.02 |  |  | V12_SOLENOID | V12 SOLENOID
|  |  | 4 | Valve-13 |  |  |  |  | CIO 1007.03 |  |  | V13_SOLENOID | V13 SOLENOID
|  |  | 5 | Valve-14 |  |  |  |  | CIO 1007.04 |  |  | V14_SOLENOID | V14 SOLENOID
|  |  | 6 | Valve-15 |  |  |  |  | CIO 1007.05 |  |  | V15_SOLENOID | V15 SOLENOID
|  |  | 7 | [5 empty] | CIO 1007.06
|  |  | 8 | [5 empty] | CIO 1007.07
|  |  | 9 | [5 empty] | CIO 1008.00
|  |  | 10 | [5 empty] | CIO 1008.01
|  |  | 11 | [5 empty] | CIO 1008.02
|  |  | 12 | [5 empty] | CIO 1008.03
|  |  | 13 | [5 empty] | CIO 1008.04
|  |  | 14 | [5 empty] | CIO 1008.05
|  |  | 15 | [5 empty] | CIO 1008.06
|  |  | 16 | [5 empty] | CIO 1008.07
|  |  | 17 | [5 empty] | CIO 1009.00
|  |  | 18 | [5 empty] | CIO 1009.01
|  |  | 19 | [5 empty] | CIO 1009.02
|  |  | 20 | [5 empty] | CIO 1009.03
|  |  | 21 | [5 empty] | CIO 1009.04
|  |  | 22 | [5 empty] | CIO 1009.05
|  |  | 23 | [5 empty] | CIO 1009.06
|  |  | 24 | [5 empty] | CIO 1009.07
|  |  | 25 | [5 empty] | CIO 1010.00
|  |  | 26 | [5 empty] | CIO 1010.01
|  |  | 27 | [5 empty] | CIO 1010.02
|  |  | 28 | [5 empty] | CIO 1010.03
|  |  | 29 | [5 empty] | CIO 1010.04
|  |  | 30 | [5 empty] | CIO 1010.05
|  |  | 31 | [5 empty] | CIO 1010.06
|  |  | 32 | [5 empty] | CIO 1010.07
| EX600 Status (Input Area) | 1 | 1 | System diagnostic status0 | The analogue input or output value has fallen below the user’s set value. |  |  |  | D 1028.00
|  |  | 2 |  | The analogue input or output value has exceeded the user’s set value. |  |  |  | D 1028.01
|  |  | 3 |  | The analogue input value has fallen below the set range. |  |  |  | D 1028.02
|  |  | 4 |  | The analogue input value has exceeded the set range. |  |  |  | D 1028.03
|  |  | 5 |  | The counter has exceeded the set value. |  |  |  | D 1028.04
|  |  | 6 |  | The open circuit has been detected. |  |  |  | D 1028.05
|  |  | 7 |  | The short circuit of the valve output or digital output has been detected. |  |  |  | D 1028.06
|  |  | 8 |  | The short circuit of the power supply for the input device has been detected. |  |  |  | D 1028.07
|  |  | 9 | System diagnostic status1 | The Power Supply for Output Device is outside specification |  |  |  | D 1029.00
|  |  | 10 |  | The power supply for control and input device is outside of the specification. |  |  |  | D 1029.01
|  |  | 11 |  | Reserved |  |  |  | D 1029.02
|  |  | 12 |  | There is a connection failure between each unit (during operation). |  |  |  | D 1029.03
|  |  | 13 |  | There is a connection failure between each unit (when the power supply is applied). |  |  |  | D 1029.04
|  |  | 14 |  | Reserved |  |  |  | D 1029.05
|  |  | 15 |  | System Error |  |  |  | D 1029.06
|  |  | 16 |  | Hardware Error |  |  |  | D 1029.07
|  |  | 17 | Unit diagnostic status 0 | Error Unit 0 |  |  |  | D 1030.00
|  |  | 18 |  | Error Unit 1 |  |  |  | D 1030.01
|  |  | 19 |  | Error Unit 2 |  |  |  | D 1030.02
|  |  | 20 |  | Error Unit 3 |  |  |  | D 1030.03
|  |  | 21 |  | Error Unit 4 |  |  |  | D 1030.04
|  |  | 22 |  | Error Unit 5 |  |  |  | D 1030.05
|  |  | 23 |  | Error Unit 6 |  |  |  | D 1030.06
|  |  | 24 |  | Error Unit 7 |  |  |  | D 1030.07
|  |  | 25 | Unit diagnostic status 1 | Error Unit 8 |  |  |  | D 1031.00
|  |  | 26 |  | Error Unit 9 |  |  |  | D 1031.01
|  |  | 27 |  | Reserved |  |  |  | D 1031.02
|  |  | 28 |  | Reserved |  |  |  | D 1031.03
|  |  | 29 |  | Reserved |  |  |  | D 1031.04
|  |  | 30 |  | Reserved |  |  |  | D 1031.05
|  |  | 31 |  | Reserved |  |  |  | D 1031.06
|  |  | 32 |  | Reserved |  |  |  | D 1031.07

## Sheet1
Name | Data Type | Address/Value | Net. Variable
G3_SP12_SPARE_INTLK | BOOL | 11.04