## GCTLR
937b Gauge Controllers

	Gauge	GTYPE	Physical Slot	Chan	ctl chan	ID	PORT
FE10B-VA-GCTLR-01	FE10B-VA-IMG-01	IMG	A	1	0
ts1_1	FE10B-VA-IMG-02	IMG	B	3	1
	FE10B-VA-PIRG-01	PIRG	C1?	5
	FE10B-VA-PIRG-02	PIRG	C2?	6
	FE10B-CS-ADC-01:CHANNEL1:VALUE	COMBINATION				01
	FE10B-CS-ADC-01:CHANNEL2:VALUE	COMBINATION				02

FE10B-VA-GCTLR-02	FE10B-VA-IMG-03	IMG	A	1	0
ts1_2	FE10B-VA-IMG-04	IMG	B	3	1
	FE10B-VA-PIRG-03	PIRG	C1?	5
	FE10B-VA-PIRG-04	PIRG	C2?	6
	FE10B-CS-ADC-02:CHANNEL1:VALUE	COMBINATION				03
	FE10B-CS-ADC-02:CHANNEL2:VALUE	COMBINATION				04

FE10B-VA-GCTLR-03	FE10B-VA-IMG-05	IMG	A	1	0
ts1_5	FE10B-VA-IMG-06	IMG	B	3	1
	FE10B-VA-PIRG-05	PIRG	C1?	5
	FE10B-VA-PIRG-06	PIRG	C2?	6
	FE10B-CS-ADC-03:CHANNEL1:VALUE	COMBINATION				05
	FE10B-CS-ADC-03:CHANNEL2:VALUE	COMBINATION				06

## MPC
Fast valve contoller

	Gauge	PUMP	SIZE
FE10B-VA-MPC-01	FE10B-VA-IONP-01	1	500
ts1_3	FE10B-VA-IONP-02	1	150
	FE10B-VA-IONP-03	2	500
	FE10B-VA-IONP-04	2	500

FE10B-VA-MPC-02	FE10B-VA-IONP-05	1	500
ts1_4	FE10B-VA-IONP-06	2	500

## VLVCC
Fast valve contoller

FE10B-CS-VLVCC-01	vlvcc_fins_port

Bit / Valve	FE Signal	FE10B-VA-ABSB-01	FE10B-VA-VALVE-01	FE10B-VA-VALVE-02	FE10B-VA-VALVE-03	FE10B-VA-VALVE-04	FE10B-VA-VALVE-05	Gauges
0	All FE Gauges/V1 closed	Air pressure	Air press. OK	Air press. OK	Air press. OK	Air press. OK	Air press. OK	IMG-01
1	IMG 1 & IonP I/L1	FE Init Vac (4of 4)	IMG-01/V1 open&Absb not closed	IMG-02/V2 open&Absb not closed	IMG-03/V3 Open	IMG-04/V4 open	V6 open	IonP-01&2 I/L 2
2		IonP-01 I/L2	IMG-02/V1 open&Absb not closed	IMG-03/V2 open&Absb not closed			V2 closed	IMG-02
3		IonP-02 I/L2	IMG-01 or IonP-1&2 I/L2					IonP-03 I/L 2
4		Water flow ABSB-02	IMG-02 or IonP-03 I/L 2					IMG-03
5		V1 not open	V5 closed					IonP-04 I/L 2
6		V2 not open					IMG-04
7		No V1 Close command					IonP-05 I/L 2
8		No V2 Close command
9
10
11
12
13
14
15		Valve movement	Valve movement	Valve movement	Valve movement	Valve movement	Valve movement

## Ports
SR10C-VA-TSERV-01
ts1_1	FE10B-VA-GCTLR-01
ts1_2	FE10B-VA-GCTLR-02
ts1_3	FE10B-VA-MPC-01
ts1_4	FE10B-VA-MPC-02
ts1_5	FE10B-VA-GCTLR-03

TCP/IP
vlvcc_fins_port	PLC
BRICK1	geobrick